## Slide 1: Power Locator
Bruce Nordman
Lawrence Berkeley National Laboratory
BNordman@LBL.gov
IETF 82 – OPSAWG
November 15, 2011

## Slide 2: Power distribution in my building
Many circuits
Many submeters
Notes: This talk to emphasize breadth, not depth.

## Slide 3: Location
How do I know “where”* in a building each specific device is?
  *“where” is location in power distribution tree
Complex buildings have many circuits and many individual devices
Knowing location needed for monitoring and control
Manual methods are possible
  Automatic would be cheaper and more reliable

## Slide 4: Sample device – PC Six days of data
Most of time, power is relatively constant
Difference provides opportunity for communication
Max power in middle of night (likely backup or similar activity)
Max is about 30% above typical / idle
Notes: This talk to emphasize breadth, not depth.

## Slide 5: Locator service example Same PC – Four hours of data
10 W signal added to ~65 W idle level
Present during alternate minutes

## Slide 6: Algorithm
Begin reading all submeters synchronously at fixed intervals
Request target device to enter locator mode with identical timing
Analyze meter data until signal is visible in one (or more) meter(s)
Terminate locator mode

## Slide 7: Synthetic submeter data – 40 PCs
Challenge: Find a 10 W signal in > 2 kW readings

## Slide 8: Submeter data – cumulative average Time series data divided into odd/even series
Averages converge to < 1 W within about 5 minutes
10 W signal easily visible

## Slide 9: Locator request details
Bitmap of signal (and length)
  can be more complex than 10101010…..
Period
  length of time of each bit
Duration
  number of periods to signal for
Can use SNMP
Mode begins immediately

## Slide 10: Thank you