## Slide 1: RPL Applicability in Industrial Networks IETF 82
draft-phinney-roll-rpl-industrial-applicability-00
Tom Phinney
Pascal Thubert
Robert Assimiti

## Slide 2: Culprits and Status
Tom Phinney, editor
  US Technical Advisor for IEC/SC 65C (http://iec.ch)
  Chair, IEC/SC 65C/WG 1 and IEC/SC 65C/MT
Robert Assimiti, co-author
  ISA100.11a co-editor (http://isa.org)
Pascal Thubert, co-author
  ISA100.11a co-editor
  ROLL/RPL co-editor

## Slide 3: Process Automation Requirements Primer
Typically utilize deterministic and centralized networks
Scalability:
  Hundreds per network
  Tens per backbone router
Extremely high reliability -> dire consequences associated with communication failure
Path diversity a must
Typically tightly time synchronized (within uSeconds)
“Shallow” wireless networks – typically up to 3 hops
Must meet latency bounds: sub-second
Relies heavily on publication/subscription (push) model for periodic data collection: as frequent as every 100 ms
Need to support for P2P control loops
Long battery life: 5 -10 years

## Slide 4: Wireless Industrial standards
Communication reliability requirements implicitly mandate path diversity for MP2P, P2MP and P2P traffic flows
Current routing paradigm in ISA100.11a and WiHART standards is DODAG based but takes place at the link-layer (mesh-under)
Graphs are computed by a system manager (centralized PCE with high degree of determinism)

## Slide 5: Traffic Classes
Safety | 0 | Emergency action | Always critical
Control | 1 | Closed loop Regulatory control | Often critical
 | 2 | Closed loop Supervisory control | Usually non-critical
 | 3 | Open loop control | Human in the loop
Monitoring | 4 | Alerting | Short-term consequences
 | 5 | Logging Downloading/uploading | No immediate consequences

## Slide 6: Data Flows
Publish/subscribe (push)
  One way, periodic communication
  Not acknowledged end-to-end
Source/sink
  Devices in set 1 send messages to devices in set 2 (alerts, alarms, etc)
  Infrequent, intermittent and bursty traffic
Peer-to-multipeer (P2MP)
Peer-to-peer (P2P)
  Device A sends data directly to devices B with high periodicity
  Allows for control-loops
Duo-cast (or N-cast)

## Slide 7: RPL MOPs versus Data Flows

## Slide 8: RPL Instances
Nodes to participate in potentially multiple RPL instances that meet different optimization goals
  Minimize and guarantee latency
  Maximize reliability
  Minimize aggregate power consumption
  Some of these optimization goals have to be met concurrently through constraints
Nodes to participate in at least one instance that has a virtual root -> allowing communications over the backbone infrastructure (subnet to subnet)

## Slide 9: Objective Functions
OF0:
  Wireless industrial communications are subject to swift and temporary variations due to the nature of the environment (metal pipe jungles) causing link related metrics to vary
  Hysteresis is needed in order to ensure stability
MRHOF
  A step in the right direction for industrial networks
  Not all metrics that need to be balanced are additive
    Example: packet success rate (ETX) for a device with rank=1 versus packet success rate (ETX) for a device with rank=3
    Look into multiplicative metrics
Need a more complex OF that:
  Takes in consideration multiple constraints
  Balances (weighted sum) multiple additive and multiplicative metrics

## Slide 10: Storing versus Non-storing Mode
Support for storing mode is imperative in wireless process automation networks
Maintaining state does not cost too much
  Typically <100 nodes per backbone router
  Shallow multi-hop networks
  Lots of devices with low rank (networks are planned and deployed that way)

## Slide 11: Food for Thought
How well does RPL interact with a centralized and deterministic paradigm?
Clock synch packets (currently link layer advertisements) need to be synched with DIO transmissions
Trickle timer considerations
DODAG repair
  Global repair – increasing the DODAG version must be subject to explicit consent from plant administrator since it could potentially result in plant shutdown
  Local repair actions need to be communicated and approved by PCE (system manager)